## Sheet1
Independence Wastewater Treatment Plant
Process Control Monitoring & Testing
Month 2006
F:M Ratios
Flow (MG) | BODinfluent (mg/l) | Vaeration (MG) | MLSS (mg/l) | F:M
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Sludge Ages
MLSS (mg/l) | Vaeration (MG) | QWAS (MGD) | WAS (mg/l) | SLUDGE
AGE (days)
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Daily Sludge Wasting Rate Based on Sludge Age
Sludge Age (days) | WAS (mg/l) | MLSS (mg/l) | Vaeration(MG) | WASTE (gpd)
20 |  |  |  | #DIV/0!
25 |  |  |  | #DIV/0!
30 |  |  |  | #DIV/0!
Daily Sludge Wasting Based on Sludge Production
Flow inf | BODinf | WAS | Sludge Yield | Sludge Solids | WASTE
mgd | mg/l | mg/l | Coefficient | lbs/day | (gpd)
|  |  | 0.5 | 0 | #DIV/0!
|  |  | 0.65 | 0 | #DIV/0!
Sludge Settling Quality
MLSS (mg/l) | 30minuteSettling | 60minuteSettling | SVI | Sludge Blanket
#DIV/0!
#DIV/0!
#DIV/0!
#DIV/0!
Note on A6: F:M Ratio is the amount of food (lbs of BOD) per lbs of solids (lbs of MLSS) under aeration.
Note on E8: An optimum F:M ratio for activated sludge (extended aeration) is .05-.10, minimum .03.
Note on C8: The total volume of the aeration basins in million gallons.
Note on D8: The aeration basins' mixed liquor suspended solids in mg/l.Use weekly or monthly average.
Note on B8: The influent BOD in mg/l. Use weekly or monthly average.
Note on A8: The influent flow to the WWTP in million gallons. Use weekly or monthly average.
Note on E17: An optimum sludge age for activated sludge (extended aeration) is 20-30 days.
Note on A15: Sludge Age is the total amount of solids in the aeration system divided by the amount wasted from the system each day. The amount of solids in the clarifier is considered negligible.
Note on A17: The aeration basins' mixed liquor suspended solids in mg/l.
Note on B17: The volume of the aeration basin in gallons
Note on C17: The flow rate of the sludge wasted each day in gallons per day.
Note on D17: The concentration of the waste activated sludge in mg/l.
Note on D42: Sludge Volume Index = ml settled sludge after 30 minutes x 1000 divided by MLSS in mg/l
Note on E42: Sludge depth in final clarifiers
Note on D34: The amount of sludge solids produced per pound of BOD treated.

## Sheet2
WWTP: Anywhere
Date
|  | F:M | Sludge Age (days) | SVI | Wasting Rate (gpd)
|  | 0.16024 | 18.722 | 260.8696 | 3744.4
Plant Flow (MGD) | 0.075
Influent BOD (mg/l) | 400
Influent BOD (lbs)
Aeration Basin Volume (MG) | 0.0814
MLSS or MLVSS (mg/l) | 2300
WAS Flow (MGD) | 0.004
WAS Concentration (mg/l) | 2500
30minute Settleable Solids | 600
Sludge Age goal (days) | 20
Aeration Basin D.O. (mg/l)
|  |  | Effluent BOD | 30
|  |  | Effluent TSS | 30
|  |  | Effluent NH3 | NA
|  |  | Effluent P | NA
Process Control
MLSS,RAS,WAS
Microscope
Flow & Loadings
F:M;Sludge Age,Wasting
D.O.
SVI
Comments: